## Power System Summary
Parameter | Value
Utility Feed Capacity (MW) | 5
Transformer TX-01 Rating (MVA) | 3.15
Transformer TX-02 Rating (MVA) | 3.15
UPS UPS-A Rating (kW) | 1000
UPS UPS-B Rating (kW) | 1000
System Power Factor | 0.9

## Earthing Calculation
Parameter | Value
Soil Resistivity (ohm-m) | 65
Fault Current (kA) | 25
Fault Duration (s) | 1
Material Constant k (A/mm2) | 80
Selected Conductor Cross-Section (mm2) | 300
Calculated Grid Resistance (ohm) | 0.48
Maximum Allowed Grid Resistance (ohm) | 1
Calculated Step Potential (V) | 610
Tolerable Step Potential (V) | 2210
Calculated Touch Potential (V) | 850
Tolerable Touch Potential (V) | 780